## Slide 1: Aggregating neighborhood space heating demand
Ina De Jaeger
Bram van der Heijde
Annelies Vandermeulen

## Slide 2: Problem statement
District energy system simulations
Trade-off between complexity and accuracy
Can we reduce amount of simulations needed to characterize heat demand of a district?
  Represent the behavior of an entire district with a few typical buildings?
l Detached
SFH
l Detached
SFH
l Detached
SFH
n Terraced
SFH
n Terraced
SFH
n Terraced
SFH
m Semi-detached
SFH
m Semi-detached
SFH
m Semi-detached
SFH
1 typical
Terraced
SFH
1 typical
Detached
SFH
1 typical
Semi-detached
SFH
?

## Slide 3: Case
City of Genk, Belgium
Two neighborhoods:
  Oud Waterschei (assuming 2000s)
  Zwartberg (North-East part, assuming 1950s)
847 buildings in total
3 archetypes per neighborhood
  Detached, semi-detached, terraced

## Slide 4
(Import)
(Export)
One-zone model
Ideal heating system
(TSet based on air temperature)
IDEAS
Geometrical data
LOD2
Statistical data for
building envelope
(Belgium)
[RWTH Aachen]
Data
Tools
CityGML
LOD2 – merged towards 8 orientations
(Export)
IBPSA - RC
Stochastic user behavior (StROBe)
OR standard user behavior
Building model - full simulation?
Notes: In a next step, I investigated the impact of the window sizes on the district energy demand. As you could see, these aren’t included in the CityGML models and thus need to be estimated.

## Slide 5: Scenarios?
Building model
  Detailed model (IDEAS)
  Reduced-order model (IBPSA)
Occupant behavior
  ISO 13790: fixed values and time schedule
  StROBe: stochastic behavior for every building
assessing the error of averaging the building geometry
different ways of determining the average set-point temperature profile

## Slide 6
Building model - archetype simulation?
3 archetypes per neighborhood > 6 archetypes
  Geometrical parameters = average of buildings
  Thermal performance parameters = identical per neighborhood
Notes: In a next step, I investigated the impact of the window sizes on the district energy demand. As you could see, these aren’t included in the CityGML models and thus need to be estimated.

## Slide 7: Optimization of ROM
modesto
  Tool to build DES optimization problems
    Energy and mass flows in time
    Choose design parameters
  Written in python
    Pyomo to construct OCP
    Gurobi/CPLEX to solve
Calculate minimum temperature profiles

## Slide 8: About temperature set-points
Imagine: two buildings with black and grey set-point

## Slide 9: About temperature set-points
Actual temperatures in buildings

## Slide 10: About temperature set-points
Leading to effective set-point profile for the average building
Result: set-point profile with a higher average temperature

## Slide 11: This is going to take a while…
To know the set-point for typical buildings
  Average minimal temperature of all separate buildings
  = simulate all buildings anyway
We tried it!
  48 core, 64 GB, =900s, full year optimization
  Takes about 10h for ~850 buildings

## Slide 12: Separate buildings vs. average building annual energy use

## Slide 13: Separate buildings vs. average building load duration curve
The rounded shape is typical for single building simulations.
It gets flattened through large number of buildings.

## Slide 14: What’s going on?

## Slide 15: What’s going on?

## Slide 16: How to reduce complexity?
Use simpler cooling model on downward step in temperature set-point profile
  Much faster, but lose some accuracy

## Slide 17: Results of simpler method
Speed-up > 10x

## Slide 18: Results of full simulation<> archetype simulation

## Slide 19: Conclusion
Averaging temperature set-points from StROBe leads to underestimation of heating demand
Averaging actual minimal building temperatures
  Annual energy use represented well
  Load duration curve has some issues
Ongoing work
  Check archetype models
  Compare with model including overheating
  Compare with simpler set-point method